THORGUARDIAN L125 / OPERATIONAL LIGHT

INSTALLATION PROCEDURE – TSB 032805

Tools Required

Adjustable Wrench, Power Drill, Electrical Tape,1/2 drill bit,5/32 drill bit, #1 & # 2 Phillips Screw Driver

Installing Light

(1)  You have  been  supplied  an LED (+12V DC)   with  a   cable  attached.  The  rated  life of  the LED exceeds   100,000  hours. All  new  factory  systems

will have the light secured directly to the bottom of the enclosure.

(2)  Remove the gasket from the light. Place the gasket against

the box, mark the location for each hole. Ensure the holes will

not interfere with the interior battery or the bracket.

(3 ) Drill each hole, and mount the light using enclosed hardware.

Installing L125

Turn off  AC  power,  disconnect  all  wires  attached  to  the battery,

and either remove battery or place black tape over Red terminal.

Disconnect  “White”  timer  control  cable  attached  to  Relay board.

Loosen mtg. hardware & remove Timer from THORGUARDIAN.

Remove L25 power cable & Sensor cable. Loosen existing L25 chassis mounting plate screws & remove L25. Remove Gray ribbon cable. Save all hardware.

Remove Existing Relay Bracket and install new “L125” Relay bracket   Reconnect all cables.

- Transfer existing  mounting screws from ( A ) to ( B ). Allow

for a 1 /4 gap do not tighten screws.

(5) Attach gray Ribbon cable to connector on the L125 label

“RELAY”. Secure with existing hardware. Attach power cable.

(6) Examine the Sensor cable connector and install in the L125 using the correct orientation. Route the LED cable between the Relay bracket and the battery and connect to the right side of the L125.

(7) Secure L125 , which is currently attached to the mounting

adapter, to the main plate. Check that no wires have been pinched.

Ensure all L125 mounting screws are tight.

(8) Connect Black wire to the lower Negative Battery Black terminal

Connect Red wire to the top Positive Battery Red terminal.

(9)Turn on AC power. This completes installation. Proceed to “L125 SETUP”

1193 Sawgrass Corporate Parkway Sunrise, Florida 33323  Tel (954) 835- 0900  Fax (954) 835 - 0808